For Official Use Only – Not for Distribution 
 6/25/2007

Emergency Action Plan (EAP)

Rock Creek Watershed, Dam No. 23
(Rock City Lake)

National Inventory of Dams (NID) No. OK11111
Coal County, Oklahoma
Coal County Conservation District
With assistance from the 
U.S. Department of Agriculture
Natural Resources Conservation Service


[image: image1]
Reviewed and Updated:

_________________________________
________________________________
Chair, Coal County Conservation District
Sheriff, Coal County,  OK
___________________
__________________
Date
Date



Copy        of  ___
Contents

Basic EAP Data
2
EAP Overview
3
Roles and Responsibilities
4
The Five-step EAP Process


Step 1
Event Detection 
5

Step 2
Emergency Level Determination
6


Guidance for Determining the Emergency Level 
7


Examples of Emergency Situations
8

Step 3
Notification and Communication
10


Notification Charts
12


Other Emergency Services Contacts
15

Step 4
Expected Actions
16

Step 5
Termination
19
Maintenance—EAP Review and Revision
20
Record of Holders of Control Copies of this EAP
21
Record of Revisions and Updates Made to EAP
22
Concurrences
23
Appendices—Forms, Glossary, Maps, and Supporting Data
24
Appendix A


Appendix A–1 
Contact Checklist
25

Appendix A–2 
Unusual or Emergency Event Log Form
26

Appendix A–3 
Dam Emergency Situation Report Form
27

Appendix A–4 
Glossary of Terms
28
Appendix B


Appendix B–1 
Resources Available
31

Appendix B–2 
Location and Vicinity Maps
32

Appendix B–3
Watershed Project Map
33

Appendix B–4 
Evacuation Map
34

Appendix B–5
Residents/Businesses/Highways at Risk
35

Appendix B–6 
Plan View of Dam
36

Appendix B–7 
Profile of Principal Spillway
37

Appendix B–8 
Reservoir Elevation-area-volume and Spillway Capacity Data
38

Appendix B–9 
National Inventory of Dams (NID) Data
39
Basic EAP Data

Purpose
The purpose of this EAP is to reduce the risk of human life loss and injury and minimize property damage during an unusual or emergency event at Rock Creek Watershed, Dam No. 23.
Potential Impacted Area 

See Evacuation Map tab (Appendix B–4) and People at Risk tab (Appendix B–5) for the locations and contact information of the following residents and businesses that may be flooded if the dam should fail and the estimated time for the flood wave to travel from the dam to these locations:

(Describe homes, businesses, and roads in downstream evacuation area)
Dam Description
Height:        ft
Drainage Area:       mi
Built:       
Hazard Classification: High
Legal Description: Sects. 14 and 23, T13N, R21W
Dam Operator: Coal County Conservation District
Latitude:         Longitude:      
Major Property Owner:      
National Inventory of Dams No.:      
Dam Designer: NRCS
See detailed design data in Appendix B tab.

Directions to dam (See Location and Vicinity Map; Appendix B–2.)

Rock Creek Watershed, Dam No. 23, can be accessed by traveling south 1.2 miles on OK Highway 44 from the Interstate 40 interchange south of Rock City; turn right (west) on a gated dirt road that goes directly to the left abutment of the dam. 

 FORMTEXT 
Keys for the lock on the gate are available from the Conservation District Manager at 523 Second Street, Rock City, OK. Note that a portion of this road is within the dam breach inundation area, and the valley below the dam may be flooded.
An alternate route to the dam is available approximately 0.5 miles south of Rock Creek on Highway 44; turn right on an ungated dirt road that goes to the right abutment of the dam. Note that Highway 44 may be inundated or the bridge may be damaged, so access to this alternate route may have to be gained from Highway 44 south of the dam.
[image: image2.jpg]STEP 1: ]
Event Detection

Step 2:
Emergency Level

EAP Overview

Detect event

v

Assess situation

determine emergency level

1

A

A 4

[

N

Determination

Step 3:
Notification and ——
Communication

Step 4:
Expected Actions —|

Step 5:
Termination
and

Level 1 Level 2 Level 3
Unusual Event; Potential Dam Urgent;
Slowly Failure Situation; Dam Failure
Developing Rapidly Appears to be
Developing Imminent or is in
Progress
A 4
Notify Notify Notify
Level 1 Level 2 Level 3
Lists Lists Lists
A 4
Monitor Save dam Save people
Protective Evacuate
Actions

Follow-up

Termination and follow-up






Roles and Responsibilities
Dam Operator’s Representative (Conservation District Manager)

•
As soon as an emergency event is observed or reported, immediately determine the emergency level (see Emergency Levels tab).


–
Level 1: unusual event, slowly developing


–
Level 2: potential dam failure situation, rapidly developing


–
Level 3: dam failure appears imminent or is in progress

•
Immediately notify the personnel in the order shown on the notification chart for the appropriate level (see Notification Charts tab).

•
Provide updates of the situation to the police/sheriff dispatcher to assist them in making timely and accurate decisions regarding warnings and evacuations.

•
Provide leadership to assure the EAP is reviewed and updated annually and copies of the revised EAP are distributed to all who received copies of the original EAP.

Incident Commander (County Sheriff)

•
Serve as the primary contact person responsible for coordination of all emergency actions. 

•
When a Level 2 situation occurs: Prepare emergency management personnel for possible evacuations that may be needed if a Level 3 situation occurs.

•
When a Level 3 situation occurs: 


–
Initiate warnings and order evacuation of people at risk downstream of the dam. 


–
Notify local emergency management services to carry out the evacuation of people and close roads within the evacuation area (see Evacuation Map tab).

•
Decide when to terminate the emergency.

•
Participate in an annual review and update of the EAP.

Emergency Management Services (Rock City)
•
Maintain communication with media.

•
When a Level 2 situation occurs:


–
Prepare emergency management personnel for possible evacuations that may be needed if a Level 3 situation occurs.


–
Alert the public as appropriate.
•
When a Level 3 situation occurs:


–
Alert the public.


–
Immediately close roads and evacuate people within the evacuation area (see Evacuation Map tab).

•
Participate in an annual review and update of the EAP.

Dam Operator’s Technical Representatives (NRCS)

•
Advise the dam operator of the emergency level determination, if time permits.

•
Advise the dam operator of remedial actions to take if Level 2 event occurs, if time permits.

State Dam Safety Agency (Oklahoma Water Resources Board)

•
Advise the dam operator of the emergency level determination, if time permits.

•
Advise the dam operator of remedial actions to take if Level 2 event occurs, if time permits.

The Five-step EAP Process

Step 1
Event Detection 

This step describes the detection of an unusual or emergency event and provides information to assist the dam operator in determining the appropriate emergency level for the event.

Unusual or emergency events may be detected by:

•
Observations at or near the dam by government personnel (local, state, or Federal), landowners, visitors to the dam, or the public

•
Evaluation of instrumentation data

•
Earthquakes felt or reported in the vicinity of the dam

•
Forewarning of conditions that may cause an unusual event or emergency event at the dam (for example, a severe weather or flash flood forecast)

See Guidance for Determining the Emergency Level table for assistance in evaluating specific events to determine if they are unusual or potential emergency situations.

Step 2
Emergency Level Determination

After an unusual or emergency event is detected or reported, the Conservation District Manager or his alternate is responsible for classifying the event into one of the following three emergency levels:

Emergency Level 1—Nonemergency, unusual event, slowly developing: 

This situation is not normal but has not yet threatened the operation or structural integrity of the dam, but possibly could if it continues to develop. NRCS technical representatives or state dam safety officials should be contacted to investigate the situation and recommend actions to take. The condition of the dam should be closely monitored, especially during storm events, to detect any development of a potential or imminent dam failure situation. The Sheriff should be informed if it is determined that the conditions may possibly develop into a worse condition that may require emergency actions.

Emergency Level 2—Potential dam failure situation, rapidly developing:

This situation may eventually lead to dam failure and flash flooding downstream, but there is not an immediate threat of dam failure. The Sheriff should be notified of this emergency situation and placed on alert. The dam operator should closely monitor the condition of the dam and periodically report the status of the situation to the Sheriff. If the dam condition worsens and failure becomes imminent, the Sheriff must be notified immediately of the change in the emergency level to evacuate the people at risk downstream.

If time permits, NRCS and state dam safety officials should be contacted to evaluate the situation and recommend remedial actions to prevent failure of the dam. The dam operator should initiate remedial repairs (note local resources that may be available—see Appendix B–1). Time available to employ remedial actions may be hours or days. 

This emergency level is also applicable when flow through the earth spillway has or is expected to result in flooding of downstream areas and people near the channel could be endangered. Emergency services should be on alert to initiate evacuations or road closures if the flooding increases.

Emergency Level 3—Urgent; dam failure appears imminent or is in progress:

This is an extremely urgent situation when a dam failure is occurring or obviously is about to occur and cannot be prevented. Flash flooding will occur downstream of the dam. This situation is also applicable when flow through the earth spillway is causing downstream flooding of people and roads. The Sheriff should be contacted immediately so emergency services can begin evacuations of all at-risk people and close roads as needed (see Evacuation Map tab).

See the following pages for guidance in determining the proper emergency level for various situations.
Guidance for Determining the Emergency Level 

	Event
	Situation
	Emergency level*

	Earth spillway flow
	Reservoir water surface elevation at auxiliary spillway crest or spillway is flowing with no active erosion 
	1

	
	Spillway flowing with active gully erosion
	2

	
	Spillway flow that could result in flooding of people downstream if the reservoir level continues to rise
	2

	
	Spillway flowing with an advancing headcut that is threatening the control section
	3

	
	Spillway flow that is flooding people downstream
	3

	Embankment overtopping
	Reservoir level is 1 foot below the top of the dam 
	2

	
	Water from the reservoir is flowing over the top of the dam 
	3

	Seepage
	New seepage areas in or near the dam
	1

	
	New seepage areas with cloudy discharge or increasing flow rate
	2

	
	Seepage with discharge greater than 10 gallons per minute
	3

	Sinkholes
	Observation of new sinkhole in reservoir area or on embankment
2
	2

	
	Rapidly enlarging sinkhole
	3

	Embankment cracking
	New cracks in the embankment greater than ¼-inch wide without seepage
	1

	
	Cracks in the embankment with seepage
	2

	Embankment movement
	Visual movement/slippage of the embankment slope
	1

	
	Sudden or rapidly proceeding slides of the embankment slopes
	3

	Instruments
	Instrumentation readings beyond predetermined values
	1

	Earthquake
	Measurable earthquake felt or reported on or within 50 miles of the dam
Earthquake resulting in uncontrolled release of water from the dam
3
	1

	
	Earthquake resulting in visible damage to the dam or appurtenances
	2

	
	Earthquake resulting in uncontrolled release of water from the dam
	3

	Security threat
	Verified bomb threat that, if carried out, could result in damage to the dam
Damage to dam or appurtenances with no impacts to the functioning of the dam
1
	2

	
	Detonated bomb that has resulted in damage to the dam or appurtenances
	3

	Sabotage/ vandalism
	Damage to dam or appurtenance with no impacts to the functioning of the dam

	1

	
	Modification to the dam or appurtenances that could adversely impact the functioning of the dam
	1

	
	Damage to dam or appurtenances that has resulted in seepage flow 
	2

	
	Damage to dam or appurtenances that has resulted in uncontrolled water release
	3


* Emergency Level 1: Nonemergency unusual event, slowly developing

* Emergency Level 2: Potential dam failure situation, rapidly developing

* Emergency Level 3: Urgent; dam failure appears imminent or is in progress

Examples of Emergency Situations

The following are examples of conditions that usually constitute an emergency situation that may occur at a dam. Adverse or unusual conditions that can cause the failure of a dam are typically related to aging or design and construction oversights. Extreme weather events that exceed the original designed conditions can cause significant flow through the auxiliary spillway or overtopping of the embankment. However, accidental or intentional damage to the dam may also result in emergency conditions. The conditions have been grouped to identify the most likely emergency-level condition. The groupings are provided as guidance only. Not all emergency conditions may be listed, and the dam operator is urged to use conservative judgment in determining whether a specific condition should be defined as an emergency situation at the dam.

Pre-existing conditions on this dam: There has been a small seepage area near the downstream toe on the north side of the release channel. This was first noticed in the 1990s, but has not changed since that time.

Earth Spillway Flows

Emergency Level 2—Potential dam failure situation; rapidly developing:
1.
Significant erosion or headcutting of the spillway is occurring, but the rate does not appear to threaten an imminent breach of the spillway crest that would result in an uncontrolled release of the reservoir.

2.
Flow through the earth auxiliary spillway is or is expected to cause flooding that could threaten people, homes, and/or roads downstream from the dam.

Emergency Level 3—Urgent; dam failure appears imminent or is in progress:

1.
Significant erosion or headcutting of the spillway is occurring at a rapid rate, and a breach of the control section appears imminent.

2.
Flow through the earth auxiliary spillway is causing flooding that is threatening people, homes, and/or roads downstream from the dam.

Embankment Overtopping 

Emergency Level 2—Potential dam failure situation; rapidly developing:
1.
The reservoir level is within 1 foot from the top of the dam.

Emergency Level 3—Urgent; dam failure appears imminent or is in progress:
1.
The reservoir level has exceeded the top of the dam, and flow is occurring over the embankment.

Seepage and Sinkholes

Emergency Level 2—Potential dam failure situation; rapidly developing:

1.
Cloudy seepage or soil deposits are observed at seepage exit points or from internal drain outlet pipes.

2.
New or increased areas of wet or muddy soils are present on the downstream slope, abutment, and/or foundation of the dam, and there is an easily detectable and unusual increase in volume of downstream seepage.

3.
Significant new or enlarging sinkhole(s) near the dam or settlement of the dam is observed.

4.
Reservoir level is falling without apparent cause.

5.
The following known dam defects are or will soon be inundated by a rise in the reservoir: 


•
Sinkhole(s) located on the upstream slope, crest, abutment, and/or foundation of the dam; or


•
Transverse cracks extending through the dam, abutments, or foundation.

Emergency Level 3—Urgent; dam failure appears imminent or is in progress:
1.
Rapidly increasing cloudy seepage or soil deposits at seepage exit points to the extent that failure appears imminent or is in progress.

2.
Rapid increase in volume of downstream seepage to the extent that failure appears imminent or is in progress.

3.
Water flowing out of holes in the downstream slope, abutment, and/or foundation of the dam to the extent that failure appears imminent or is in progress.

4.
Whirlpools or other evidence exists indicating that the reservoir is draining rapidly through the dam or foundation.

5.
Rapidly enlarging sinkhole(s) are forming on the dam or abutments to the extent that failure appears imminent or is in progress.

6.
Rapidly increasing flow through crack(s) eroding materials to the extent that failure appears imminent or is in progress.

Embankment Movement and Cracking

Emergency Level 2—Potential dam failure situation; rapidly developing:

1.
Settlement of the crest, slopes, abutments and/or foundation of the dam that may eventually result in breaching of the dam.

2.
Significant increase in length, width, or offset of cracks in the crest, slopes, abutments, and/or foundation of the dam that may eventually result in breaching of the dam.

Emergency Level 3—Urgent; dam failure appears imminent or is in progress:

1.
Sudden or rapidly proceeding slides, settlement, or cracking of the embankment crest, slopes, abutments, and/or foundation, and breaching of the dam appears imminent or is in progress.

Step 3
Notification and Communication

Notification 

After the emergency level has been determined, the people on the following notification charts for the appropriate emergency level shall be notified immediately. 

Communication
Emergency Level 1—Nonemergency, unusual event; slowly developing:

The Conservation District Manager and NRCS District Conservationist should contact the NRCS State Conservation Engineer and Oklahoma Water Resources Board. Describe the situation, and request technical assistance on next steps to take.

Emergency Level 2—Emergency event, potential dam failure situation; rapidly developing: 

The following message may be used to help describe the emergency situation to the Sheriff or Rock City emergency management personnel:


“This is _____Identify yourself; name, position)_________. 


We have an emergency condition at Rock Creek Watershed, Dam No. 23, located 2 miles south of Rock City. 


We have activated the Emergency Action Plan for this dam and are currently under Emergency Level 2.


We are implementing predetermined actions to respond to a rapidly developing situation that could result in dam failure.


Please prepare to evacuate the area along low-lying portions of Rock Creek. 


Reference the evacuation map in your copy of the Emergency Action Plan. 

 
We will advise you when the situation is resolved or if the situation gets worse.


I can be contacted at the following number ___________________. If you cannot reach me, please call the following alternative number ___________________.”

Emergency Level 3—Urgent event; dam failure appears imminent or is in progress:
The Sheriff should be contacted immediately and the area evacuated (see Evacuation Map tab). The following actions should be taken:

1.
Call the Sheriff’s dispatch center. Be sure to say, “This is an emergency.” They will call other authorities and the media and begin the evacuation. The following message may be used to help describe the emergency situation to the Sheriff or Rock City emergency management personnel:


“This is an emergency. This is _____Identify yourself; name, position)_________. 


Rock Creek Watershed, Dam No. 23, located 2 miles south of Rock City, is failing. The downstream area must be evacuated immediately. Repeat, Rock Creek Watershed, Dam No. 23, is failing; evacuate the area along low-lying portions of Rock Creek. 


We have activated the Emergency Action Plan for this dam and are currently under Emergency Level 3. Reference the evacuation map in your copy of the Emergency Action Plan. 


I can be contacted at the following number ___________________. If you cannot reach me, please call the following alternative number___________________.”

2.
Do whatever is necessary to bring people in immediate danger (anyone on the dam, downstream from the dam, boating on the reservoir, or evacuees) to safety if directed by the Sheriff.

3.
Keep in frequent contact with the Sheriff and emergency services to keep them up-to-date on the condition of the dam. They will tell you how you can help handle the emergency. 

4.
If all means of communication are lost: (1) try to find out why, (2) try to get to another radio or telephone that works, or (3) get someone else to try to re-establish communications. If these means fail, handle the immediate problems as well as you can, and periodically try to re-establish contact with the Sheriff and emergency services. 

The following prescripted message may be used as a guide for the Sheriff or Rock City emergency services personnel to communicate the status of the emergency with the public:  


Attention:  This is an emergency message from the Sheriff. Listen carefully. Your life may depend on immediate action. 


Rock Creek Watershed, Dam No. 23, located 2 miles south of Rock City, is failing. Repeat. Rock Creek Watershed, Dam No. 23, located 2 miles south of Rock City, is failing. 


If you are in or near this area, proceed immediately to high ground away from the valley. Do not travel on Highway 44 south of Rock City or return to your home to recover your possessions. You cannot outrun or drive away from the flood wave. Proceed immediately to high ground away from the valley.

Repeat message.
Emergency Level 1 Notifications
Nonemergency

unusual event; slowly developing



Emergency Level 2 Notifications
Emergency event, potential dam failure

situation; rapidly developing


Emergency Level 3 Notifications
Urgent event, dam failure appears 

imminent or is in progress



Emergency Services Contacts
	Agency / Organization
	Principal contact
	Address
	Office telephone number
	Alternate telephone numbers

	Coal County Board of Supervisors
	Gloria Brown, Chair
	336 Highway 66
Rock City, OK
	407–555–XXXX
	407–555–XXXX

	Coal County Road Department
	Max Gray, Supervisor
	973 Ninth Street 
Rock City, OK
	407–555–XXXX
	407–555–XXXX

	Coal County Conservation District
	John Jordon * 
District Manager
	523 Second Street
Rock City, OK
	407–555–XXXX
	407–555–XXXX (H)
407–555–XXXX (C)

	Coal County Conservation District
	Mary James *
District Secretary
	523 Second Street
Rock City, OK
	407–555–XXXX
	407–555–XXXX (H)
407–555–XXXX (C)

	Coal County Conservation District
	Mike Blain *
Board Chair
	523 Second Street
Rock City, OK
	407–555–XXXX
	407–555–XXXX (H)
407–555–XXXX (C)

	Coal County Sheriff
	Henry Martin
	336 Highway 66
Rock City, OK
	407–555–XXXX
	407–555–XXXX (H)
407–555–XXXX (C)

	Dry Gulch Television Station KJMT
	Chris Klinger
Manager
	5632 Main Street
Dry Gulch, OK
	407–555–XXXX
	407–555–XXXX

	Landowner of Dam No. 23
	Bryon Babcock
	R.R. #2
Rock City, OK
	
	407–555–XXXX (H)
407–555–XXXX (C)

	National Weather Service
	Danny Lee  Climatologist
	66374 Elm Street
Norman, OK
	618–555–XXXX
	407–555–XXXX

	Natural Resources Conservation Service
	Shelly Winters
District Conservationist
	523 Second Street
Rock City, OK
	407–555–XXXX
	407–555–XXXX (H)
405–555–XXXX (C)

	Natural Resources Conservation Service
	John Blake *
Technician
	523 Second Street
Rock City, OK
	407–555–XXXX
	407–555–XXXX (H)

	Natural Resources Conservation Service
	Robert Redford
State Engineer
	3458 Farm Road
Strong City, OK
	917–555–XXXX
	917–555–XXXX (H)
917–555–XXXX (C)

	Oklahoma Department of Transportation
	Bill Dobson
District Engineer
	539 Center Street
Dry Gulch, OK
	407–555–XXXX
	

	Oklahoma Highway Patrol
	Richard Barnell
	299 First Avenue
Dry Gulch, OK
	407–555–XXXX
	

	Oklahoma Water Resources Board 
	Joe Griswold
Dam Safety Officer
	1522 Maple Avenue
Strong City, OK
	618–555–XXXX
	618–555–XXXX (H)
618–555–XXXX (C)

	Rock City Emergency Management Coordinator
	Jeff Powers
	121 Main Street
Rock City, OK
	407–555–XXXX
	

	Rock City Fire Department
	Harry James
	336 Maple Street
Rock City, OK
	407–555–XXXX
	

	Rock City Police
	Red Jones
	336 Maple Street
Rock City, OK
	407–555–XXXX
	

	Rock City Radio Station 1040 AM 
	Scott Fagen
Manager
	667 Eighth Street
Rock City, OK
	407–555–XXXX
	


* Back-up to primary contact

Step 4
Expected Actions

If the police or Sheriff receives a 911 call regarding observations of an unusual or emergency event at the dam, they should immediately contact the Conservation District office. After the Conservation District Manager determines the emergency level, the following actions should be taken. If time permits, NRCS and the Oklahoma Water Resources Board should be contacted for technical consultation. 

Emergency Level 1—Nonemergency, unusual event; slowly developing:
A.
The Conservation District Manager should inspect the dam. At a minimum, inspect the full length of the upstream slope, crest, downstream toe, and downstream slope. Also, check the reservoir area, abutments, and downstream channel for signs of changing conditions. If increased seepage, erosion, cracking, or settlement are observed, immediately report the observed conditions to the NRCS or the Oklahoma Water Resources Board; refer to the emergency level table for guidance in determining the appropriate event level for the new condition and recommended actions.
B.
Record all contacts that were made on the Contact Checklist (Appendix A–1). Record all information, observations, and actions taken on the Event Log Form (Appendix A–2). Note the time of changing conditions. Document the situation with photographs and video, if possible.

C.
The Conservation District Manager should contact NRCS and request technical staff to investigate the situation and recommend corrective actions.

Emergency Level 2—Potential dam failure situation; rapidly developing:

A.
The Conservation District Manager should contact the NRCS and the Oklahoma Water Resources Board to report the situation and, if time permits, request technical staff to investigate the situation and recommend corrective actions. 

B.
The Conservation District Manager should contact the sheriff to inform him/her that the EAP has been activated and if current conditions get worse, an emergency situation may require evacuation. Preparations should be made for possible road closures and evacuations.

C.
Provide updates to the Sheriff and emergency services personnel to assist them in making timely decisions concerning the need for warnings, road closures, and evacuations.

D.
If time permits, the Conservation District Manager should inspect the dam. At a minimum, inspect the full length of the upstream slope, crest, downstream toe, and downstream slope. Also, check the reservoir area, abutments, and downstream channel for signs of changing conditions. If piping, increased seepage, erosion, cracking, or settlement are observed, immediately report the observed conditions to the NRCS and the Oklahoma Water Resources Board; refer to the emergency level table for guidance in determining the appropriate event level for the new condition and recommended actions.

E.
Record all contacts that were made on the Contact Checklist (Appendix A–1). Record all information, observations, and actions taken on the Event Log Form (Appendix A–2). Note the time of changing conditions. Document the situation with photographs and video, if possible.

F.
If time permits, the following emergency remedial actions should be taken as appropriate.
Emergency Level 2—Potential dam failure situation; rapidly developing—continued:

Emergency remedial actions
If time permits, the following emergency remedial actions should be considered for Emergency Level 2 conditions. Immediate implementation of these remedial actions may delay, moderate, or prevent the failure of the dam. Several of the listed adverse or unusual conditions may be apparent at the dam at the same time, requiring implementation of several modes of remedial actions. Close monitoring of the dam must be maintained to confirm the success of any remedial action taken at the dam. Time permitting, any remedial action should be developed through consultation with NRCS and the Oklahoma Water Resources Board. See Resources Available (Appendix B–1) for sources of equipment and materials to assist with remedial actions.

Embankment overtopping 

1.
If the water level in the reservoir is no longer rising, place sandbags along the low areas of the top of the dam to control wave action, reduce the likelihood of flow concentration during minor overtopping, and to safely direct more water through the spillway.

2.
Cover the weak areas of the top of the dam and downstream slope with riprap, sandbags, plastic sheets, or other materials to provide erosion-resistant protection.

Seepage and sinkholes
1.
Open the principal spillway gate to lower the reservoir level as rapidly as possible to a level that stops or decreases the seepage to a nonerosive velocity. If the gate is damaged or blocked, pumping or siphoning may be required. 


Continue lowering the water level until the seepage stops.

2.
If the entrance to the seepage origination point is observed in the reservoir (possible whirlpool) and is accessible, attempt to reduce the flow by plugging the entrance with readily available materials such as hay bales, bentonite, soil or rockfill, or plastic sheeting.

3.
Cover the seepage exit area(s) with several feet of sand/gravel to hold fine-grained embankment or foundation materials in place. Alternatively, construct sandbag or other types of ring dikes around seepage exit areas to retain a pool of water, providing backpressure and reducing the erosive nature of the seepage.

4.
Prevent vehicles and equipment from driving between the seepage exit points and the embankment to avoid potential loss from the collapse of an underground void.

Embankment movement
1.
Open outlet(s) and lower the reservoir to a safe level at a rate commensurate with the urgency and severity of the condition of the slide or slump. If the gate is damaged or blocked, pumping or siphoning may be required.

2.
Repair settlement of the crest by placing sandbags or earth and rockfill materials in the damaged area to restore freeboard.

3.
Stabilize slides by placing a soil or rockfill buttress against the toe of the slide.

Earthquake
1.
Immediately conduct a general overall visual inspection of the dam. 

2.
Perform a field survey to determine if there has been any settlement and movement of the dam embankment, spillway, and low-level outlet works.

3.
Drain the reservoir, if required. 

Emergency Level 3—Urgent; dam failure appears imminent or is in progress:
A.
The Conservation District Manager shall immediately contact the Sheriff and others shown on the notification chart.

B.
The Sheriff shall lead the efforts to carry out warnings, close roads, and evacuate people at risk downstream from the dam (see Evacuation Map tab).

C.
Emergency management services personnel shall alert the public and immediately evacuate at-risk people and close roads as necessary.

D.
The Conservation District Manager shall maintain continuous communication and provide the Sheriff with updates of the situation to assist him/her in making timely decisions concerning warnings and evacuations. 

E.
The Conservation District Manager should record all contacts that were made on the Contact Checklist (Appendix A–1). Record all information, observations, and actions taken on the Event Log Form (Appendix A–2). Note the time of changing conditions. Document the situation with photographs and video, if possible.

F.
Advise people monitoring the dam to follow safe procedures. Everyone should stay away from any of the failing structures or slopes and out of the potential breach inundation areas.

Step 5
Termination

Whenever the EAP has been activated, an emergency level has been declared, all EAP actions have been completed, and the emergency is over, the EAP operations must eventually be terminated and follow-up procedures completed. 

Termination responsibilities
The Sheriff is responsible for terminating EAP operations and relaying this decision to the Conservation District Manager. It is then the responsibility of each person to notify the same group of contacts that were notified during the original event notification process to inform those people that the event has been terminated.

Prior to termination of an Emergency Level 3 event that has not caused actual dam failure, the NRCS technical representative or the State Dam Safety Officer will inspect the dam or require the inspection of the dam to determine whether any damage has occurred that could potentially result in loss of life, injury, or property damage. If it is determined that conditions do not pose a threat to people or property, the Sheriff will be advised to terminate EAP operations as described above.

The Conservation District Manager shall assure that the Dam Safety Emergency Situation Report (Appendix A–3) is completed to document the emergency event and all actions that were taken. The Conservation District shall distribute copies of the completed report to the Oklahoma Water Resources Board and the NRCS State Conservation Engineer.

Maintenance—EAP Review and Revision

EAP annual review
The Conservation District Manager will review and, if needed, update the EAP at least once each year. The EAP annual review will include the following:

•
Calling all contacts on the three notification charts in the EAP to verify that the phone numbers and persons in the specified positions are current. The EAP will be revised if any of the contacts have changed.

•
Contacting the local law enforcement agency to verify the phone numbers and persons in the specified positions. In addition, the Conservation District Manager will ask if the person contacted knows where the EAP is kept and if responsibilities described in the EAP are understood.

•
Calling the locally available resources to verify that the phone numbers, addresses, and services are current.

Revisions

The Conservation District is responsible for updating the EAP document. The EAP document held by the Conservation District is the master document. When revisions occur, the Conservation District will provide the revised pages and a revised revision summary page to all the EAP document holders. The document holders are responsible for revising outdated copy of the respective document(s) whenever revisions are received. Outdated pages shall be immediately discarded to avoid any confusion with the revisions. 

EAP periodic test
The Conservation District will host and facilitate a periodic test of the EAP at least once every 5 years.

The periodic test will consist of a meeting, including a tabletop exercise, conducted at the Coal County Conservation District office. Attendance should include the Conservation District Manager, key conservation district staff members, NRCS staff, at least one representative of the local law enforcement agency, and others with key responsibilities listed in the EAP. At the discretion of the Conservation District, other organizations that may be involved with an unusual or emergency event at the dam are encouraged to participate. Before the tabletop exercise begins, meeting participants will visit the dam during the periodic test to familiarize themselves with the dam site.

The tabletop exercise will begin with the facilitator presenting a scenario of an unusual or emergency event at the dam. The scenario will be developed prior to the exercise. Once the scenario has been presented, the participants will discuss the responses and actions that they would take to address and resolve the scenario. The narrator will control the discussion, ensuring realistic responses and developing the scenario throughout the exercise. The Conservation District Manager should complete an event log as they would during an actual event.

After the tabletop exercise, the five sections of the EAP will be reviewed and discussed. Mutual aid agreements and other emergency procedures can be discussed. The Conservation District will prepare a written summary of the periodic test and revise the EAP, as necessary. 

Record of Holders of Control Copies of this EAP

	Copy Number
	Organization
	Person receiving copy

	1
	Coal County Conservation District

523 Second Street
Rock City, OK 50010
	John Jordan

	2
	Coal County Conservation District

523 Second Street
Rock City, OK 50010
	Mike Blain

	3
	NRCS Field Office
523 Second Street
Rock City, OK 50010
	Shelly Winters

	4
	NRCS State Office
3458 Farm Road
Strong City, OK 51020
	Robert Redford

	5
	Coal County Sheriff’s Department
336 Highway 66
Rock City, OK 50010
	Henry Martin

	6
	Rock City Emergency Management
121 Main Street
Rock City, OK 50010
	Jeff Powers

	7
	Rock City Police Department
336 Maple Street
Rock City, OK 50010
	Red Jones

	8
	Oklahoma Water Resources Board
1522 Maple Street
Strong, OK 50010
	Joe Griswold


Record of Revisions and Updates Made to EAP

	Revision Number
	Date
	Revisions made
	By whom

	1

	6–25–07
	Updated 6–25–07 EAP with current contact information for Conservation District personnel and names of new residents in evacuation area
	John Jordon



Concurrences

By my signature, I acknowledge that I, or my representative, have reviewed this plan and concur with the tasks and responsibilities assigned herein for me and my organization.

1.____________________________________________________________________________________

                           Signature                                               Organization                                                            Date

Printed name and title:  Mike Blain, Chair, Coal County Conservation District

2. ___________________________________________________________________________________
                           Signature                                               Organization                                                            Date

Printed name and title:  Henry Martin, Sheriff, Coal County
3.____________________________________________________________________________________

                           Signature                                               Organization                                                            Date

Printed name and title:  Jeff Powers, Emergency Management Coordinator, Rock City
4.____________________________________________________________________________________

                           Signature                                               Organization                                                            Date

Printed name and title:  Red Jones, Chief of Police, Rock City
5.____________________________________________________________________________________

                           Signature                                               Organization                                                            Date

Printed name and title:  Shelley Winters, District Conservationist, NRCS, Rock City
6.____________________________________________________________________________________

                           Signature                                               Organization                                                            Date

Printed name and title:___________________________________________________________________

7.____________________________________________________________________________________

                           Signature                                               Organization                                                            Date

Printed name and title: __________________________________________________________________

Appendices—Forms, Glossary, Maps, and 
Supporting Data

Appendix A

A–1
Contact Checklist

A–2
Unusual or Emergency Event Log Form

A–3
Dam Emergency Situation Report Form

A–4
Glossary of Terms

Appendix B

B–1
Resources Available 

B–2
Location and Vicinity Maps

B–3
Watershed Project Map

B–4
Evacuation Map

B–5
Residents/Businesses/Highways at Risk

B–6
Plan View of Dam

B–7
Profile of Principal Spillway

B–8
Reservoir Elevation-Area-Volume and Spillway Capacity Data

B–9
National Inventory of Dams (NID) Data

Appendix A–1

Contact Checklist

Rock Creek Watershed, Dam No. 23
Coal County, Oklahoma
Date _____________   

The following contacts should be made immediately after the emergency level is determined (see pages 
7–10 for guidance to determine the appropriate emergency level for a specific situation). The person making the contacts should initial and record the time of the call and who was notified for each contact made. See the Notification Charts tab for critical contact information and Emer. Services Contacts tab for contact information for other possible emergency services.

Emergency Level 1 (see page 12)
Person
Time
Contacted 


Contacted
Contacted
by

___ NRCS District Conservationist
_____________
_____________
_____________
___ NRCS State Conservation Engineer
_____________
_____________
_____________
___ Oklahoma Water Resources Board
_____________
_____________
_____________
Emergency Level 2 (see page 13)
Person
Time
Contacted


Contacted
Contacted
by

____ NRCS District Conservationist  
_____________
_____________
_____________
____ NRCS State Conservation Engineer 
_____________
_____________
_____________
____ Oklahoma Water Resources Board
_____________
_____________
_____________
____ Sheriff
_____________
_____________
_____________
Emergency Level 3 (see page 14)
Person  
Time
Contacted


Contacted
Contacted
by

____ Sheriff
_____________
_____________
_____________
____ Oklahoma Water Resources Board
_____________
_____________
_____________
____ NRCS District Conservationist 
_____________
_____________
_____________
____ NRCS State Conservation Engineer
_____________
_____________
_____________
Appendix A–2

Unusual or Emergency Event Log

(to be completed during the emergency)

Dam name:     Rock Creek Watershed, Dam No. 23                          County:       Coal County
When and how was the event detected? _____________________________________________________________________________
_____________________________________________________________________________
Weather conditions: _____________________________________________________________
_____________________________________________________________________________
General description of the emergency situation: _____________________________________________________________________________
_____________________________________________________________________________
_____________________________________________________________________________
Emergency level determination: ______________  Made by: ____________________________
Actions and Event Progression
	Date
	Time
	Action/event progression
	Taken by

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	


Report prepared by: _______________________________________  Date: _______________

Appendix A–3

Dam Emergency Situation Report

(to be completed following the termination of the emergency)

Dam name:  Rock Creek Watershed, Dam No. 23

National Inventory of Dams (NID) No.: OK11111
Dam location:  2 miles south of Rock City                    Coal County          Rock Creek       
                                (City)                                              (County)                (Stream/River)

Date:       
Time:      


Weather conditions: ____________________________________________________________
General description of emergency situation: _____________________________________________________________________________
_____________________________________________________________________________
Area(s) of dam affected: _____________________________________________________________________________
_____________________________________________________________________________
Extent of dam damage:  _________________________________________________________
Possible cause(s): ______________________________________________________________
Effect on dam’s operation:_______________________________________________________
Initial reservoir elevation: _______________________
Time: ______________
Maximum reservoir elevation: ______________________
Time: ______________
Final reservoir elevation: _________________________
Time: ______________
Description of area flooded downstream/damages/injuries/loss of life: ____________________
______________________________________________________________________________
______________________________________________________________________________
Other data and comments: ______________________________________________________________________________
Observer’s name and telephone number:_________________________________________
Report prepared by: ________________________________________    Date: ______________
Appendix A–4
Glossary of Terms


Abutment
That part of the valleyside against which the dam is constructed. The left and right abutments of dams are defined with the observer looking downstream from the dam.


Acre-foot
A unit of volumetric measure that would cover 1 acre to a depth of 1 foot. One acre-foot is equal to 43,560 cubic feet or 325,850 gallons.


Berm
A nearly horizontal step (bench) in the upstream or downstream sloping face of the dam.


Boil
A disruption of the soil surface due to water discharging from below the surface. Eroded soil may be deposited in the form of a ring (miniature volcano) around the disruption.


Breach
An opening through the dam that allows draining of the reservoir. A controlled breach is an intentionally constructed opening. An uncontrolled breach is an unintended failure of the dam.


Conduit
A closed channel (round pipe or rectangular box) that conveys water through, around, or under the dam.


Control section
A usually level segment in the profile of an open channel spillway above which water in the reservoir discharges through the spillway.


Cross section
A slice through the dam showing elevation vertically and direction of natural water flow horizontally from left to right. Also, a slice through a spillway showing elevation vertically and left and right sides of the spillway looking downstream.


Dam
An artificial barrier generally constructed across a watercourse for the purpose of impounding or diverting water.


Dam failure
The uncontrolled release of a dam’s impounded water. 


Dam Operator
The person(s) or unit(s) of government with responsibility for the operation and maintenance of dam.

Drain, toe or foundation,
A water collection system of sand and gravel and typically pipes along the

or blanket
downstream portion of the dam to collect seepage and convey it to a safe outlet.


Drainage area (watershed)
The geographic area on which rainfall flows into the dam.


Drawdown
The lowering or releasing of the water level in a reservoir over time or the volume lowered or released over a particular period of time.


Emergency
A condition that develops unexpectedly, endangers the structural integrity of the dam and/or downstream human life and property, and requires immediate action.


Emergency Action Plan
A formal document identifying potential emergency conditions that may

(EAP) 
occur at the dam and specifying preplanned actions to minimize potential failure of the dam or minimize failure consequences including loss of life, property damage, and environmental impacts.


Evacuation map
A map showing the geographic area downstream of a dam that should be evacuated if it is threatened to be flooded by a breach of the dam or other large discharge.


Filter
The layers of sand and gravel in a drain that allow seepage through an embankment to discharge into the drain without eroding the embankment soil.


Freeboard
Vertical distance between a stated water level in the reservoir and the top of dam.


Gate, slide or sluice, 
An operable, watertight valve to manage the discharge of water from the 

or regulating 
dam.


Groin
The area along the intersection of the face of a dam and the abutment.


Hazard classification
A system that categorizes dams (high, significant, or low) according to the degree of their potential to create adverse incremental consequences such as loss of life, property damage, or environmental impacts of a failure or misoperation of a dam. 


Height, dam
The vertical distance between the lowest point along the top of the dam and the lowest point at the downstream toe, which usually occurs in the bed of the outlet channel.


Hydrograph, inflow or 
A graphical representation of either the flow rate or flow depth at a specific 

outflow, or breach 
point above or below the dam over time for a specific flood occurrence.


Incident Commander
The highest predetermined official available at the scene of an emergency situation.


Instrumentation
An arrangement of devices installed into or near dams that provide measurements to evaluate the structural behavior and other performance parameters of the dam and appurtenant structures.


Inundation area or map
The geographic area downstream of the dam that would be flooded by a breach of the dam or other large discharge.


Notification
To immediately inform appropriate individuals, organizations, or agencies about a potentially emergency situation so they can initiate appropriate actions.


Outlet works
An appurtenant structure that provides for controlled passage of normal 

(principal spillway)
water flows through the dam. 


Piping
The progressive destruction of an embankment or embankment foundation by internal erosion of the soil by seepage flows.


Probable Maximum 
The theoretically greatest precipitation or resulting flood that is 


Precipitation (PMP) or 
meteorologically feasible for a given duration over a specific drainage area 


Flood (PMF) 
at a particular geographical location.


Reservoir
The body of water impounded or potentially impounded by the dam.


Riprap
A layer of large rock, precast blocks, bags of cement, or other suitable material, generally placed on an embankment or along a watercourse as protection against wave action, erosion, or scour.


Risk
A measure of the likelihood and severity of an adverse consequence.


Seepage
The natural movement of water through the embankment, foundation, or abutments of the dam.


Slide
The movement of a mass of earth down a slope on the embankment or abutment of the dam.

Spillway (auxiliary 
The appurtenant structure that provides the controlled conveyance of

or emergency) 
excess water through, over, or around the dam.


Spillway capacity
The maximum discharge the spillway can safely convey with the reservoir at the maximum design elevation.


Spillway crest
The lowest level at which reservoir water can flow into the spillway.


Tailwater
The body of water immediately downstream of the embankment at a specific point in time.


Toe of dam
The junction of the upstream or downstream face of an embankment with the ground surface. 


Top of dam (crest of dam)
The elevation of the uppermost surface of an embankment which can safely impound water behind the dam.
Appendix B–1
Resources Available

Locally available equipment, labor, and materials:

The County Commissioners have the following resources that can be utilized in the event of an emergency: 

•
two front-end loaders

•
two backhoes

•
one track hoe

•
two graders

•
two dump trucks

•
a sand borrow pit

•
a clay borrow pit
Contact the Coal County Road Department—see Emer. Services Contacts tab.

Other locally available resources include:


	Heavy equipment service
and rental
	Sand and gravel supply


	 Ready-mix concrete supply



	Bob’s Dozer Service
134 Elm Street
Rock City, OK
407–555–XXXX
	Kern’s Sand and Gravel
R.R. 2
Rock City, OK
407–555–XXXX
	Burnett Concrete Co.
231 Sixth Street
Dry Gulch, OK
407–555–XXXX

	
	
	

	Tiller Construction Co.
405 Second Street
Dry Gulch, OK
407–555–XXXX
	Renfro Sand Products
334 Aston Avenue
Spring Lake, OK
407–555–XXXX
	

	
	
	

	Pumps
	Diving contractor
	Sand bags

	A to Z Rental
569 Seventh Street
Rock City, OK
407–555–XXXX
	Steve White
2201 56th Street
Johnstown, OK
917–555–XXXX
	A to Z Rental
5643 Water Street
Johnstown, OK 
917–555–XXXX


Appendix B–2
Location and Vicinity Maps
(Insert map)
Appendix B–3
Watershed Project Map

(Insert map)
Appendix B–4
Evacuation Map
(Insert map)
Appendix B–5
Residents/Businesses/Highways at Risk

A major flood caused by a sudden breach of the dam is estimated to inundate six homes, three businesses, and three highways. These homes and businesses (marked on the evacuation map) are located east of OK Highway 44 and south of Chestnut Street in Rock City. 

	House/
business no.* 
	Resident/business 
	Address


	Phone no.


	Distance downstream from dam
(ft)
	Travel time**
(hr)
	Max water depth above first floor (ft)

	   1 
	Fred and Ethel James
	10300 132nd Street 
	555–XXXX
	5,000 
	0.3
	5.4

	  B-2
	Larry’s Hardware
	3214 Chestnut Street
	555–XXXX
	11,400
	0.9
	0.8

	  B-3
	Lori’s Music Shop
	2288 Farm Road
	555–XXXX
	11,600
	0.9
	2.6

	  B-4
	Bill’s Coffee Shop
	1455 Sugar Street
	555–XXXX
	11,800
	1.0
	4.8

	   5 
	Terry and Ann Smith 
	4812 Chestnut Street
	555–XXXX
	13,600
	1.1
	3.0

	   6 
	Amos Hill 
	5500 Apple Road
	555–XXXX
	14,000 
	1.1
	3.2

	   7 
	Allen and Ruth Jones 
	4814 Chestnut Street
	555–XXXX
	13,800 
	1.1
	1.2

	   8 
	Mike and Carol Green 
	4902 Chestnut Street
	555–XXXX
	14,000 
	1.1
	2.4

	   9 
	Stephanie Evans 
	4910 Chestnut Street
	555–XXXX
	14,200 
	1.1
	0.5

	
	OK Highway 44
	
	
	  2,000
	0.2
	7.9

	
	Interstate 40
	
	
	10,000
	0.8
	3.4

	
	OK Route 66
	
	
	11,200
	0.9
	3.4


* See Appendix B–4.

** Estimated time for breach wave (peak) to travel from dam to downstream locations

Basis for computation of evacuation area and flooding depths

Breach inundation study completed by NRCS–August 2004
Hydraulic model used: NRCS TR–20 (routing); TR–60 (peak discharge); TR–66 (hydrograph) 

Model assumptions:


“Sunny Day” Breach (no inflow into the reservoir)


Water surface elevation in reservoir prior to breach = _______ (top of dam)


Total volume of breach hydrograph = ______ acre-ft


Height of water at time of breach = ______ ft


Peak breach discharge = _______ ft3/s


Downstream area defined by field surveys consisting of 10 cross sections and 3 bridge openings

Appendix B–6
Plan View of Dam

(Insert map)

Appendix B–7
Profile of Principal Spillway
(Insert map)
Appendix B–8
Reservoir Elevation-area-volume 
and Spillway Capacity Data

ROCK CREEK WATERSHED 
DAM NO. 23
	Elevation
	Reservoir Surface acres
	Reservoir Storage acre ft
	Spillway Discharge
ft3/s

	1682.0
	0.0
	0.0
	0

	1684.0
	0.3
	0.3
	0

	1686.0
	2.0
	2.5
	0

	1688.0
	3.7
	8.2
	0

	1690.0
	8.6
	20.5
	0

	1692.0
	15.9
	45.0
	0

	1694.0
	18.7
	79.6
	9

	1696.0
	23.5
	121.8
	0

	Principal Spillway Crest

	1697.0
	26.2
	146.7
	0

	1698.0
	31.1
	175.4
	45

	1700.0
	40.8
	247.3
	76

	1702.0
	49.3
	337.4
	82

	1704.0
	62.0
	448.7
	87

	1706.0
	71.4
	582.1
	92

	1708.0
	86.7
	740.2
	97

	1710.0
	98.6
	925.5
	102

	Auxiliary Spillway Crest

	1712.0
	115.0
	1139.1
	108

	1714.0
	129.9
	1384.0
	516

	1716.0
	145.3
	1659.2
	2090

	1718.0
	160.7
	1965.2
	4437

	1720.0
	178.8
	2304.7
	7763

	

	1720.2
	180.6
	2340.6
	7937


Appendix B–9
National Inventory of Dams (NID) Data
Dam name: ________

State: ________ 
 
NID ID: ________ 

Longitude:– ________ 

Latitude: ________

Geodetic location: ________ 


County: ________

Stream: ________ 

Nearest town: ________

Distance to nearest town: ___ mi

Operator: ________ Cons. District

Year constructed: ________ 



Max. discharge: ____ ft3/s 

Max. storage: _____acre-ft 

Normal storage: _____ acre-ft 

Surface area: ___ acre 

Drainage area: ___ mi2 



Inspection frequency: 1 yr 

State regulated?: Yes 

State reg. agency: ________
Federal funding: USDA NRCS

Federal design: USDA NRCS
Federal constructed: USDA NRCS

Program authority: Flood prevention
Watershed No.: _____
Watershed name: ________
Service life: ___ yr

O&M insp. resp.: ________ Cons. District
O&M insp. current?: _____
Population at risk: __
Dam height: ____ ft

Dam length: _____ ft

Dam volume: _____ yd3 

Design hazard potential: ____
Current hazard potential: _____ 

Hazard potential class. year: ____
Sediment storage: ____ acre-ft

Flood storage: _____ acre-ft

Surcharge storage: ____ acre-ft

Other storage: ____ acre-ft

Principal spillway type: Concrete pipe
Principal spillway conduit diameter: ___ in 

Auxiliary spillway type: Vegetated earth
Auxiliary spillway width: _____ ft
Dam Operator’s Rep.


Conservation District Manager


� FORMTEXT ��John Jordan�


� FORMTEXT ��407–555–XXXX�(Office)


� FORMTEXT ��407–555–XXXX�(Home)


� FORMTEXT ��407–555–XXXX� (Cell)





State Dam Safety Official





Oklahoma Water �Resources Board


� FORMTEXT ��Joe Griswold�


� FORMTEXT ��618–555–XXXX� (Office)


� FORMTEXT ��618–555–XXXX� (Home)


� FORMTEXT ��618–555–XXXX� (Cell)

















Insert local area map showing specific location of dam








Note:


1, 2, etc., denotes call sequence





Legend:


Calls by operator 	 ______


Second level calls - - - - - 





See Emer. Services Contacts tab for contact


 information for back-ups to the persons shown above


 and other emergency personnel.





Dam Operator’s Rep.


� FORMTEXT ��Coal County� Conservation District Manager


� FORMTEXT ��John Jordan�


� FORMTEXT ��407-555-XXXX� (Office)


� FORMTEXT ��407-555-XXXX� (Home)


� FORMTEXT ��407-555-XXXX� (Cell)





(2)





Incident Commander


Sheriff


� FORMTEXT ��Henry Martin�


� FORMTEXT ��407–555–XXXX� (Office)


� FORMTEXT ��407–555–XXXX� (Home)





(2)





� FORMTEXT ��Rock City� Emergency


Management 


Dispatcher





NRCS State Engineer


� FORMTEXT ��Robert Redford�


� FORMTEXT ��917–555–XXXX� (Office)


� FORMTEXT ��917–555–XXXX� (Home)


� FORMTEXT ��917–555–XXXX� (Cell)





� FORMTEXT ��OK� Highway Patrol 


Dispatcher





Coal County Amateur


Radio Association:


� FORMTEXT ��John Turney�


� FORMTEXT ��KE5GBD�


� FORMTEXT ��407–555–XXXX� 





� FORMTEXT ��Rock City� Police


Dispatcher





National Weather Service


� FORMTEXT ��618–555–XXXX�





Note:


1, 2, etc., denotes call sequence





Legend:


Calls by operator  _______ 


Second level calls - - - - - - 





See Emer. Services Contacts tab for contact information for back-ups to the persons shown above and other emergency personnel.  





See Communications tab for prescripted messages.








Insert state map showing location of dam





Incident Commander


Sheriff


� FORMTEXT ��Henry Martin�


� FORMTEXT ��407-555-XXXX� (Office)


� FORMTEXT ��407-555-XXXX� (Home)


Or


24-HOUR 911





� FORMTEXT ��OK� Highway Patrol 


Dispatcher





� FORMTEXT ��Rock City� Police


Dispatcher





Dam Operator’s


Technical Reps.


NRCS District Conservationist


� FORMTEXT ��Shelly Winters�


� FORMTEXT ��407–555–XXXX� (Office)


� FORMTEXT ��407–555–XXXX� (Home)


� FORMTEXT ��407–555–XXXX� (Cell)








NRCS State Engineer


� FORMTEXT ��Robert Redford�


� FORMTEXT ��917–555–XXXX� (Office)


� FORMTEXT ��917–555–XXXX� (Home)


� FORMTEXT ��917–555–XXXX� (Cell)





National Weather Service


� FORMTEXT ��618–555–XXXX�





Dam Operator’s


Technical Reps.


NRCS District Conservationist


� FORMTEXT ��Shelly Winters�


� FORMTEXT ��407–555–XXXX� (Office)


� FORMTEXT ��407–555–XXXX� (Home)


� FORMTEXT ��407–555–XXXX� (Cell)





See Emer. Services Contacts tab for contact information for back-ups to the persons shown above and other emergency personnel.  








Dam Operator’s


Technical Reps.


NRCS District Conservationist


� FORMTEXT ��Shelly Winters�


� FORMTEXT ��407–555–XXXX� (Office)


� FORMTEXT ��407–555–XXXX� (Home)


� FORMTEXT ��407–555–XXXX� (Cell)





NRCS State Engineer


� FORMTEXT ��Robert Redford�





� FORMTEXT ��917–555–XXXX� (Office)


� FORMTEXT ��917–555–XXXX� (Home)


� FORMTEXT ��917–555–XXXX� (Cell)





State Dam Safety


Official


Oklahoma Water Resources Board


� FORMTEXT ��Joe Griswold�


� FORMTEXT ��618–555–XXXX� (Office)


� FORMTEXT ��618–555–XXXX� (Home)


� FORMTEXT ��618–555–XXXX� (Cell)





Note:


1, 2, etc., denotes call sequence





Legend


Calls by operator _______


Second level calls - - - - - 





� FORMTEXT ��Rock City� Emergency


Management 


Dispatcher





Dam Operator’s Rep.


� FORMTEXT ��Coal County� Conservation District Manager


� FORMTEXT ��John Jordan�


� FORMTEXT ��407–555–XXXX� (Office)


� FORMTEXT ��407–555–XXXX� (Home)


� FORMTEXT ��407–555–XXXX� (Cell)





State Dam Safety Official





Oklahoma Water


Resources Board


� FORMTEXT ��Joe Griswold�


� FORMTEXT ��618–555–XXXX� (Office)


� FORMTEXT ��618–555–XXXX� (Home)


� FORMTEXT ��618–555–XXXX� (Cell)





Coal County Amateur


Radio Association:


� FORMTEXT ��John Turney�


� FORMTEXT ��KE5GBD�


� FORMTEXT ��407–555–XXXX� 





See Communications tab


 for prescripted messages.





(1)





(1)





(3)





(3)





(2)





(1)





Incident Commander


Sheriff


� FORMTEXT ��Henry Martin�


� FORMTEXT ��407–555–XXXX� (Office)


� FORMTEXT ��407–555–XXXX� (Home)


� FORMTEXT ��407–555–XXXX� (Cell)


or


24-Hour 911















Rock Creek Watershed, Dam No. 23, Coal County, OK– NID OK1111
PAGE  
 
Rock Creek Watershed, Dam No. 23, Coal County, OK– NID OK1111

