## TitlePage
DRINKING WATER MANAGEMENT PLAN
FOR
School Building Code:
School District:
Date Published:
Next Update (Annually):
Published by:
Name
Contact Phone#:
Revisions (dates):

## Instructions
INSTRUCTIONS FOR COMPLETING THIS WORKBOOK
This document is a tool that may be used to assist schools in the development of a drinking water management and flushing plan. Two Michigan Department of Environment, Great Lakes, and Energy (EGLE) flushing guidance documents, the High Velocity Method and the Fresh Tap Method, provide the narrative for the flushing tabs in this plan. A plumbing assessment and mapping of fixtures is needed to complete this form.
This workbook consists of the following tabs:
Plan Information
Use this tab to identify water management team members, their roles, and responsibilities. Identifying personnel establishes accountability.
Basic Building Info
Use this tab to record general information about the building. The EGLE Plumbing Profile document is a more comprehensive tool that also contains this information. For the Profile, go to Michigan.gov/SchoolWater.
System Maintenance Plan
Use this tab as a general schedule for when a water maintenance activity needs to be done. The schedule will be based on the condition and age of the system as well as water use patterns. The facility manager is to determine this schedule.
General Plumbing Info
Use this tab to record the plumbing information gathered from the building walk-through. The cells have a pop up message with instructions.
Fixture Code Info
This is an information page on how to develop a coding system for individual fixtures. Establishing a code helps identify outlets used for consumption (drinking or cooking) and can be used for flushing and sampling purposes.
Fixture Inventory
Use this tab to record all the outlets used for consumption (drinking, food preparation, cooking, teeth brushing). Do not include other outlets.
Flushing Zone Tabs
There are four tabs included in this workbook for flushing zone information. Zones are determined using the EGLE Pre-Flushing Event Guidance for School Plumbing and EGLE Guidance for Flushing School Plumbing (High Velocity Method) documents. Every building will have at least one zone (Flushing Zone #1). If only one zone, ignore or delete the other flushing zone tabs. Use additional tabs for each zone and if there are more than three zones, copy the FlushingZoneToDuplicate tab. Go to Michigan.gov/SchoolWater for the reference document.
High Velocity Flush Method
This tab gives you the steps for conducting the high velocity flushing method. Some cells are automatically filled in for you with information provided on other tabs. Go to Michigan.gov/SchoolWater for the document.
Fresh Tap Method
This tab gives you the steps for conducting the fresh tap flushing method. Some cells are automatically filled in for you with information provided on other tabs. Go to Michigan.gov/SchoolWater for the document.
Flushing Log
Use this tab for recording the flushing events.
O&M Costs
This is a simplistic form for recording costs associated with the water maintenance plan.
Service Line Calculation
This is an example with information on how to calculate the length of the service line.

## PlanInformation
MAINTENANCE PLAN INFORMATION
Goals: |  | Key Concerns:
1. Provide healthy water |  | Stagnant water
2. Extend life of plumbing system |  | Plumbing material
3. Reduce costs |  | Plumbing integrity
Build up on pipe interior
Changes in source water - disinfection levels, corrosion control treatment
System breech - introduction of contaminants
Maintenance Actions/Activities:
Water system flushing
Water outlet flushing
POE filter replacement
POU filter replacement
Cleaning or replacement of aerators/screens/strainers on fixtures
Cleaning and maintenance of water use devices and appliances* |  |  | *An appliance would be a coffee, soda, ice machine, etc. A device is a softener, etc.
Replacement of fixtures, valves, and other plumbing items
Acronyms & Information:
POE (Point of Entry)
POU (Point of Use)
Preventive Maintenance - Planned and carried out on a regular basis to maintain and keep infrastructure in good condition.
Corrective Maintenance - Replacing or reparing something done incorrectly or needing change for improvement.
Emergency Maintenance - Reaction to a crisis or public complaints normally due to failure, malfunction, or breakdown of equipment.
Periodic Maintenance - Infrequent actions needed, for example biannual, once in ten years, etc.
Roles & Responsibilities:
Name | Title |  | Responsibility

## BasicBuildingInfo
PLUMBING ASSESSMENT - BASIC BUILDING INFORMATION
DESCRIPTION | DATA ENTRY
SCHOOL DISTRICT
SCHOOL BUILDING NAME
BUILDING CODE
STREET ADDRESS
CITY
ZIP
COUNTY
SCHOOL TYPE
GRADE LEVELS
TOTAL STUDENT POPULATION
ORIGINAL YEAR BUILT
DATES OF ADDITIONS
ADDITIONAL CONNECTIONS
BLUE PRINTS AVAILABLE
NAME OF WATER SUPPLIER
BUILDING CONTACT PERSON
TITLE
PHONE (OFFICE)
PHONE (CELL)
DATE FORM COMPLETED
FUTURE REVIEW DATE
ADDITIONAL INFORMATION OR COMMENTS

## SystemMaintenancePlan
GENERAL WATER SYSTEM MAINTENANCE PLAN
Task | Estimated Time to Complete | Scheduled Time
|  | Daily | Weekly | Monthly | Quarterly | Semi-Annual | Annual | Other
Initial plumbing assessment
Plumbing assessment update/review
Inspect plumbing system (leaks, etc.)
High Velocity Flush
Fresh Tap Flush
Filter inspection
Filter replacement
Aerator, screen, strainer inspection
Water use device inspection
Water use device replacement
Water appliance inspection
Water appliance replacement
Equipment & Material Needs
Item |  | Total # | # Spares on Hand | Order Frequency | # Needed to Order | Comments
POE replacement filter cartridges
POU replacement filter cartridges-Fixture
POU replacement filter cartridges-Fountain
Fixture Aerators or screens
Strainers
Company Contacts |  | Phone# |  | Email |  | Notes

## GeneralPlumbingInfo
GENERAL WATER AND PLUMBING INFORMATI0N
DESCRIPTION | [5 empty] | UNITS
Location water enters the building
How many points of service line entries are there into this building?
Service line material (pipe coming in)
Service line diameter (POE pipe) | [5 empty] | Inches
Length of service line to street or well | [5 empty] | Feet
Diameter of pipe from water meter to first outlet | [5 empty] | Inches
Length of pipe from water meter to first outlet | [5 empty] | Feet
Calculated volume of service line | [5 empty] | Gallons
Point of entry water treatment
| Water Softener |  |  | Phosphate
| Filtration System |  |  | Chlorine
| None |  |  | Other
Water tanks & heaters |  | Types
Locations
Cold-water pipe materials (inside building)
Lead solder present
Water fixture closest to POE |  | ID# |  |  | Location
First fixture flow rate |  | Volume of container = | Units of measure = | L | Time to fill (sec)= |  | gpm
Amt. of time to flush entire service line | [5 empty] | Minutes
Building regions (may also be zones or parts of zones)
Number of floors
Number of wings
Connected buildings
Total regions
Water fixture furthest point |  | ID# |  |  | Location
All cells that allow data to be entered must have a value for the formulas to work. Be sure to at least enter a zero in the cell if there is no other value.

## FixtureCodeInfo
THIS IS AN INFORMATION PAGE - NO DATA ENTRY NEEDED
GENERATING A FIXTURE ID CODE
It is important to generate a unique code for each outlet used for consumption for sampling and flushing plans. Using the unique code for sampling helps to match all test results with the specific location so that any remediation needed can be done quickly.
Sequence Number (SEQ#):
This is the order in which you take samples, with #1 being the tap closest to the service connection and the first sample you collect. The sequence should follow the flow of cold water through building as best can be determined.
Codes for Outlet Types
DF |  | Drinking Fountain (non-refrigerated)
WC |  | Water Cooler (plug-in chiller unit - refrigerated unit)
B |  | Drinking Water Bubbler (at classroom sink)
BF |  | Bottle Fill (the spout at a bottle fill station or at another type of bottle filling appliance that is connected to the water supply)
CF |  | Classroom Faucet (for consumption)
KF |  | Kitchen Sink Faucet (cooking or food prep)
KK |  | Kitchen Kettle (cold water fill)
IM |  | Ice Machine
RF |  | Restroom Faucet
TL |  | Teacher's Lounge Faucet
NS |  | Nurse's Office Sink Faucet
SC |  | Service Connection (closest tap to the service line, not necessarily a tap for consumption)
Additional Codes for First-Draw and Flush Samples
Add a "P" at the end of the Fixture ID Code to indicate a first-draw sample at a tap
Add an "F" at the end of the Fixture ID Code to indicate a 30-second or a 15-minute flush sample collected
| Example: First draw WE-110-B-P |  |  | Flush: WE-110-B-F
EXAMPLE: Washington Middle School |  |  |  |  | EXAMPLE: South Elementary School
SEQ# | Fixture ID Code |  | Fixture Location | Tap Type | SEQ# | Fixture ID Code | Fixture Location | Tap Type
1 | WMS-110Hall-DF |  | Hall near room 110 | Drinking fountain | 1 | SE-100-B | Room 100 | Bubbler
2 | WMS-GymL-WC |  | Gym (lower unit) | Water cooler | 2 | SE-100-CF | Room 100 | Classroom faucet
3 | WMS-GymH-WC |  | Gym (high unit) | Water cooler | 3 | SE-102-B | Room 102 | Bubbler
4 | WMS-HE1-CF |  | Home economics room | Classroom faucet | 4 | SE-102-CF | Room 102 | Classroom faucet
5 | WMS-HE2-CF |  | Home economics room | Classroom faucet | 5 | SE-DF1 | First floor | Drinking fountain
6 | WMS-Kit-KK |  | Kitchen | Kitchen kettle | 6 | SE-DF2 | Second floor | Drinking fountain
7 | WMS-WC2-B |  | Hall near main office | Bubbler | 7 | SE-KIT1-KF | Kitchen | Faucet
8 | WMS-WC2-BF |  | Hall near main office | Bottle Fill | 8 | SE-KIT2-KF | Kitchen | Faucet
9 | WMS-WC3-B |  | Hall near library | Bubbler | 9 | SE-KIT1-KK | Kitchen | Kettle fill
10 | WMS-WC3-BF |  | Hall near library | Bottle Fill | 10 | SE-KIT2-KK | Kitchen | Kettle fill
SAMPLE ONLY COLD WATER AT TAPS FOR DRINKING OR CONSUMPTION - Do not sample other water outlets.
*EGLE recommends action to reduce the risk of lead in drinking water on any individual fixtures with test results greater than 0.005 mg/L for lead and 1.3 mg/L for copper.

## FixtureInventory
Drinking & Food Preparation Fixture Inventory
SEQUENCE # | FIXTURE ID CODE | FIXTURE LOCATION | TAP TYPE CODE | BRAND MAKE/MODEL # | CHILLER UNIT? | BRASS VALVES? | FILTER? | AERATOR OR SCREEN? | MOTION ACTIVATED? | FIXTURE WORKS? | CORROSION? | DISCOLORED WATER? | LEAKING? | COMMENTS

## FlushingZone#1
HIGH VELOCITY FLUSHING ZONE
Reference: EGLE Pre-Flushing Event Guidance for School Plumbing and EGLE Guidance for Flushing School Plumbing (High Velocity Method)
Please read the guidance documents prior to conducting the pre-flushing and flushing tasks.
Steps to Determing Zones
Step | Action
1 | Conduct a building walk-through to determine flow of cold water to each fixture and map on floor plan.
2 | Look at floor plan for "visual zones" such as # of floors, wings, additions, room groupings, etc.
3 | Conduct a trial run to see if you get 3 ft/sec through the meter by opening fixtures for each zone. Adjust zones as needed.
4 | Attach the map of the school building with each flushing zone color coded and numbered (see example in reference document)
ZONE #1
Water fixture closest to POE in this zone |  | ID# | 0 | Location | 0
Water fixture furthest point in this zone |  | ID# |  | Location
Total number of faucets including kitchen, classroom, laboratory faucets, teacher lounge, office, and nurses in this zone (both consumption and nonconsumption)
Total number of classroom bubblers in this zone
Total number of restroom handwashing faucets in this zone
Total number of shower heads in this zone
Total number of toilets in this zone
Total number of janitor faucets in this zone
Total number of non-refrigerated drinking fountains in this zone without a filter
Total Number of FAUCETS, OTHER OUTLETS, & NON-REFRIGERATED DRINKING FOUNTAINS in this Zone
Total number of non-refrigerated drinking fountains in this zone with a filter
Total number of refrigerated drinking fountains in this zone with a filter
Total number of refrigerated drinking fountains in this zone without a filter
Total Number of FILTERED Drinking Fountain Taps in this Zone
Note: Enter a zero (0) for any fixture(s) that do not exist

## FlushingZone#2
HIGH VELOCITY FLUSHING ZONE
Reference: EGLE Pre-Flushing Event Guidance for School Plumbing and EGLE Guidance for Flushing School Plumbing (High Velocity Method)
Please read the guidance documents prior to conducting the pre-flushing and flushing tasks.
Steps to Determing Zones
Step | Action
1 | Conduct a building walk-through to determine flow of cold water to each fixture and map on floor plan.
2 | Look at floor plan for "visual zones" such as # of floors, wings, additions, room groupings, etc.
3 | Conduct a trial run to see if you get 3 ft/sec through the meter by opening fixtures for each zone. Adjust zones as needed.
4 | Attach the map of the school building with each flushing zone color coded and numbered (see example in reference document)
ZONE #2
Water fixture closest to POE in this zone |  | ID# | Location
Water fixture furthest point in this zone |  | ID# | Location
Total number of faucets including kitchen, classroom, laboratory faucets, teacher lounge, office, and nurses in this zone (both consumption and nonconsumption)
Total number of classroom bubblers in this zone
Total number of restroom handwashing faucets in this zone
Total number of shower heads in this zone
Total number of toilets in this zone
Total number of janitor faucets in this zone
Total number of non-refrigerated drinking fountains in this zone without a filter
Total Number of FAUCETS, OTHER OUTLETS, & NON-REFRIGERATED DRINKING FOUNTAINS in this Zone
Total number of non-refrigerated drinking fountains in this zone with a filter
Total number of refrigerated drinking fountains in this zone with a filter
Total number of refrigerated drinking fountains in this zone without a filter
Total Number of FILTERED Drinking Fountain Taps in this Zone
Note: Enter a zero (0) for any fixture(s) that do not exist

## FlushingZone#3
HIGH VELOCITY FLUSHING ZONE
Reference: EGLE Pre-Flushing Event Guidance for School Plumbing and EGLE Guidance for Flushing School Plumbing (High Velocity Method)
Please read the guidance documents prior to conducting the pre-flushing and flushing tasks.
Steps to Determing Zones
Step | Action
1 | Conduct a building walk-through to determine flow of cold water to each fixture and map on floor plan.
2 | Look at floor plan for "visual zones" such as # of floors, wings, additions, room groupings, etc.
3 | Conduct a trial run to see if you get 3 ft/sec through the meter by opening fixtures for each zone. Adjust zones as needed.
4 | Attach the map of the school building with each flushing zone color coded and numbered (see example in reference document).
ZONE #3
Water fixture closest to POE in this zone |  | ID# | Location
Water fixture furthest point in this zone |  | ID# | Location
Total number of faucets including kitchen, classroom, laboratory faucets, teacher lounge, office, and nurses in this zone (both consumption and nonconsumption)
Total number of classroom bubblers in this zone
Total number of restroom handwashing faucets in this zone
Total number of shower heads in this zone
Total number of toilets in this zone
Total number of janitor faucets in this zone
Total number of non-refrigerated drinking fountains in this zone without a filter
Total Number of FAUCETS, OTHER OUTLETS, & NON-REFRIGERATED DRINKING FOUNTAINS in this Zone
Total number of non-refrigerated drinking fountains in this zone with a filter
Total number of refrigerated drinking fountains in this zone with a filter
Total number of refrigerated drinking fountains in this zone without a filter
Total Number of FILTERED Drinking Fountain Taps in this Zone
Note: Enter a zero (0) for any fixture(s) that do not exist

## FlushingZoneToDuplicate
HIGH VELOCITY FLUSHING ZONE
Reference: EGLE Pre-Flushing Event Guidance for School Plumbing and EGLE Guidance for Flushing School Plumbing (High Velocity Method)
Please read the guidance documents prior to conducting the pre-flushing and flushing tasks.
Steps to Determing Zones
Step | Action
1 | Conduct a building walk-through to determine flow of cold water to each fixture and map on floor plan.
2 | Look at floor plan for "visual zones" such as # of floors, wings, additions, room groupings, etc.
3 | Conduct a trial run to see if you get 3 ft/sec through the meter by opening fixtures for each zone. Adjust zones as needed.
4 | Attach the map of the school building with each flushing zone color coded and numbered (see example in reference document).
ZONE #
Water fixture closest to POE in this zone |  |  | ID# | Location
Water fixture furthest point in this zone |  |  | ID# | Location
Total number of faucets including kitchen, classroom, laboratory faucets, teacher lounge, office, and nurses in this zone (both consumption and nonconsumption)
Total number of classroom bubblers in this zone
Total number of restroom handwashing faucets in this zone
Total number of shower heads in this zone
Total number of toilets in this zone
Total number of janitor faucets in this zone
Total number of non-refrigerated drinking fountains in this zone without a filter
Total Number of FAUCETS, OTHER OUTLETS, & NON-REFRIGERATED DRINKING FOUNTAINS in this Zone
Total number of non-refrigerated drinking fountains in this zone with a filter
Total number of refrigerated drinking fountains in this zone with a filter
Total number of refrigerated drinking fountains in this zone without a filter
Total Number of FILTERED Drinking Fountain Taps in this Zone
Note: Enter a zero (0) for any fixture(s) that do not exist
Steps to duplicate this sheet if there are more than 4 flushing zones:
| 1 | Right click on the FlushingZoneToDuplicate tab at the bottom
| 2 | Click on "Move or Copy"
| 3 | Scroll down the list & click on FlushingZoneToDuplicate
| 4 | Click on the box at the lower left that says "Create a Copy"
| 5 | Click "Ok"
| 6 | Right click on the new tab and rename it to the appropriate flushing zone number
| 7 | On the sheet go to cell A11 and type in the zone number

## HighVelocityFlushMethod
HIGH VELOCITY FLUSHING METHOD PROCEDURES
This flushing method involves moving the water in zones at all water fixtures including toilets, handsinks, etc.
The procedure is to open all the taps in a zone, let the water run for 15 minutes, then move to the next zone and repeat the process.
Reference: EGLE Guidance for Flushing School Plumbing (High Velocity Method) *READ THOUGHLY BEFORE CONDUCTING FLUSHING
Use the building floor plan and zone map(s) to assist in this process.
Zone Flushing |  | Total Number of Zones: | Estimated Total Flush Time(minutes):
STEP | ACTION (More than one person required)
1 | Start flushing hot water tank(s) in utility room (flush until cold water comes out of tank)
2 | Go to first zone (closest to the service line)
3 | Remove any aerators, strainers, or screens
4 | Fully open the cold water side of fixtures
5 | Systematically flush all toilets
6 | Record initial reading at the meter
7 | Time one minute and record a second reading at the meter
8 | If flow rate is close to or equal to 3 ft/sec through the meter start the flushing timer for this zone
9 | Flush this zone for 15 minutes. Monitor flow rate at least three times during flush period.
10 | Adjust zone size if needed - if flow rate is below 3ft/sec, open more fixtures; if above 3 ft/sec, close some fixtures
11 | Close all fixtures in this zone (clean and replace aerators, strainers, and screens)
12 | Go to next zone, repeat steps 3-11 until all zones are flushed (no need to flush hot water tank again)
NOTE: Keep a record of the calculated flow rates obtained during the flushing process for each zone, time of zone flushing, and problems noted.
Do not use filtered bottle fill drinking fountains or other inline filtered drinking fountains as a flushing point.

## FreshTapFlushMethod
FRESH TAP FLUSHING METHOD PROCEDURE
The fresh tap flushing method involves bringing fresh cold water to every fixture used for drinking or food preparation.
The procedure is to open the tap one at a time and let the water run for a specified time to get fresh cold water to the tap.
Reference: EGLE School Building Flushing Best Practices (Fresh Tap Method) for detailed information. *READ THOUGHLY BEFORE CONDUCTING FLUSHING
Use the building floor plan with fixture locations to assist in this process and make sure every drinking/food prep tap is flushed.
STEP | ACTION
1 | Go to fixture closest to POE |  | ID# | 0 |  |  | Location | 0
2 | Remove aerator or screen
3 | Fully open the cold water side of fixture
4 | Run cold water for |  | minutes
5 | Turn off fixture
6 | Clean and replace aerator or screen and re-install
7 | Go to fixture farthest from POE |  | ID# | 0 |  |  | Location | 0
8 | Remove aerator or screen
9 | Fully open the cold water side of fixture
10 | Run cold water for |  | minutes (can determine precise amount of time based on calculation of lenth of pipe and flow rate of this tap)
11 | Turn off fixture
12 | Clean and replace aerator or screen and re-install
If multiple floors and/or wings, conduct steps 7-12 on each
13 | Working your way back to the POE, flush every consumptive fixture except for the non-filtered refrigerated fountains one at at time for:
seconds
14 | Flush non-filtered refrigerated fountains for 15 minutes
15 | Run water through appliances connected to the water supply such as pop machines, coffee machines, etc.
DETERMINING TOTAL FLUSHING EVENT TIME
Number of consumptive fixtures (not including non-filtered refrigerated):
|  | Time to flush consumptive fixtures: |  |  |  | minutes
| Number of non-filtered refrigerated drinking fountains: | [7 empty] | Time to flush: | minutes
| Total flushing event time |  |  |  | minutes | Note: Include about five minutes for aerator removal/replacement at each fixture
| Estimated time to walk to each fixture during the process | [5 empty] | minutes
| Estimated time from beginning to end including walk time | [5 empty] | minutes |  | Time in hours:
Do not use filtered refrigerated bottle fill drinking fountains for a 15 minute flushing point.
Note: Be aware not to overload wastewater drains during tap flushing. Record event on the Flushing Log (see FlushingLog tab).
All cells that allow data to be entered must have a value for the formulas to work. Be sure to at least enter a zero in the cell if there is no other value.

## FlushingLog
FLUSHING LOG
MONTH: |  | STAFF NAME (PRINT):
STAFF SIGNATURE:
Flushing Sequence | FixtureID Code | Fixture Location | Date | Time | Duration of Flushing | Comments

## O&MCosts
OPERATION & MAINTENANCE COSTS
| Unit Cost | Total # Needed | Total Cost | Time on Task | Initial Install Cost | Replacement Cost | Notes
Labor Costs
Water Use Costs
Sewer Use Costs
Fixture replacement
Faucet type
Faucet type
Faucet type
Plumbing repairs
Filter replacement
Drinking fountains
Bottle fill stations
Faucet POU
Filter installation
Drinking fountains
Bottle fill stations
Faucet POU
Drinking Fountain
Refrigerated DF

## ServiceLineCalculation
Service Line Calculation Example
15 Feet
28 Feet
32 Feet
Rough calculation of the length of service line for this example: 15+28+32= 75 Feet
School or Child Care Center Building
Road
Service Line
Watermain
Water in (POE)
Watermeter
Outlet closest to service line

## Sheet2 (hide tab) (hidden)
TITLE | SCHOOL TYPE | Units of Measure
Administrator | Child Care | gal
Director of Operations | PreSchool | L
Facility Director | Elementary | qt
Maintenance Supervisor | Middle
Other (specify) | Junior High
High
Alternative
Combo
Other (Specify)
YEAR BUILT | ADDITIONS? | ADDITIONAL WATER LINE CONNECTIONS:
Pre-1950 | Yes | None
1950-1959 | No | Concession Stand
1960-1969 | Unknown | Athletic Field(s)
1970-1979 |  | Other (specify)
1980-1989
1990-2014
2015 to current year
Unknown
CLOSE/FAR TAP FLUSH TIME | TAP FLUSH TIMES | Material Type
10 | 30 | Lead
15 | 60 | Copper
20 | 120 | Galvanized
25 | 180 | Ductile iron
30 | 240 | Plastic
60 | 300 | Unknown
Other